## Equipment log
Hotel equipment maintenance log
One line for anything done to a piece of equipment, planned or repair. Date, initials and real readings on every line. No blank lines: write "not done" and why.
Date | Asset | Tag | Location | What was done | Type (planned or repair) | Done by (initials) | Parts used | Cost | Readings | Next due
3 Nov | Generator | GEN-1 | Generator room | Weekly test run, 15 minutes. Fuel, oil and coolant checked. | Planned | VH |  |  | Hours 1,412. Fuel 3/4. | 10 Nov
3 Nov | AC unit | AC-214 | Room 214 | Filter washed and refitted. Airflow checked. | Planned | PM |  |  | Outlet 13 C | 3 Dec
4 Nov | AC unit | AC-421 | Room 421 | Water dripping from indoor unit. Drain line blocked, cleared and flushed. | Repair | PM
5 Nov | Pool pump | PP-1 | Pool | Basket emptied, pressure checked, no leaks. | Planned | VH |  |  | Filter 14 psi | 12 Nov
From https://turndownhq.com/guides/hotel-maintenance-log-template/ . Free to copy and use at your property.

## Daily rounds
Hotel equipment maintenance log
Date: ________ Morning round by: ____ Time: ____ Afternoon: ____ Time: ____ Night: ____ Time: ____
Write the reading, not a tick. Anything out of the ordinary: write it in Notes and raise a work order.
Area | Check | Morning | Afternoon | Night | Notes or work order
Plant room | Water supply pressure (gauge reading)
Plant room | Tank levels, float valves free
Plant room | Pumps start and stop on pressure, no leaks, no new noise
Plant room | Water treatment or softener: salt, filter pressure, alarms
Hot water | Storage temperature (reading)
Hot water | Return temperature (reading)
Hot water | Burners or elements normal, no fault lights, no gas smell
Hot water | Relief valve discharge pipes dry
Generator | Fuel level (reading)
Generator | Charger on, no alarms, switch on automatic, no leaks
Fire safety | Panel normal, no faults or disabled zones
Fire safety | Exit routes clear, exit signs lit, fire doors closing
Kitchen | Walk-in cooler temperature (reading)
Kitchen | Freezer temperature (reading)
Kitchen | Door seals closing, no ice on evaporators, drains clear
Kitchen | Ice machine making ice, bin clean
Laundry | Dryer lint screens cleaned, no leaks, no gas smell
Pool and spa | Chemistry done and logged in the pool log (by whom)
Pool and spa | Pump running, filter pressure normal, gate self-closing
Roof and outside | AC condensers running, coils clear of debris
Roof and outside | Roof drains and gutters clear
Roof and outside | Outside lights on timer, car park and paths lit
Public areas | Lobby, corridors, restrooms: lights, temperature, smells
Public areas | Elevator in service
Public areas | Automatic doors working, no trip hazards
Night round | Exterior doors locked, perimeter lights, pool gate locked
From https://turndownhq.com/guides/hotel-maintenance-log-template/ . Free to copy and use at your property.